[image: image1.png]\u_—€=====5

COUNTY
Certified Unified Program Agency





[Type here]

	[image: image1.png]
	Mike Lee
Director – Community Development & Services Agency
Clark Pickell

Director – Environmental Health & CUPA
Government Center 915 8th Street, Suite 123

Marysville, California 95901-5273

(530) 749-5450 Fax (530) 749-5454



	Facility      
	Owner       

	Address       
	Address       

	                    
	                    

	Phone      
	Phone       

	Contractor      
	Analytical Lab       

	Address       
	Address       

	                    
	                    

	Phone       
	Phone       

	
	Tank 1
	Tank 2
	Tank 3
	Tank 4

	Size of Tanks
	      
	     
	     
	     

	Contents
	     
	     
	     
	     

	REMOVAL REQUIREMENTS

	1.  All residual liquid, solids, and/or sludge shall be removed and handled as a hazardous waste or

recyclable material in accordance with 6.5 of the Health and Safety Code.

	2.  Tanks shall be made inert prior to excavation and removal to below 10% LEL using dry ice at a 

rate of 30 lbs./1000 gallons.

	3.  Associated piping must be flushed, excavated, removed, and properly disposed of, unless 
Deemed unfeasible by the CUPA.  If unfeasible, piping must be capped.

	4.  Sampling must be conducted according to sampling requirements.

	5.  All site work must be in accordance with OSHA standards, and safe business practices.

	TANK DISPOSAL OPTIONS (Designate one)

	 FORMCHECKBOX 
 TREATMENT, STORAGE, AND/OR

 DISPOSAL FACILITY (TSDF)--Tanks shall be 

manifested and hauled by a licensed hauler to an

EPA permitted TSDF.  A copy of the manifest 

must be submitted within 30 days.
	 FORMCHECKBOX 
SPECIFIC REUSE—tanks are destined for a 

specific reuse which must be designated by the 

owner of the tank. Reuse does not allow for 

cutting of the tank, or otherwise compromising the

integrity of the tank. If tanks are not in good

condition upon removal, reuse will not be allowed

and disposal at a TSDF must be made within 5 

days.

	Hauler:       
	New Owner:       

	Hauler EPA#       
	Address:       

	Address:      
	                     

	                    
	Phone:       

	Phone:       
	Nature of Reuse:      

	Designated TSDF      
	     

	Address:      
	     

	                    
	     

	Phone:      
	     


Underground Storage Tank Program - Application for Removal

	Note:  Fire Departments may require removal permit, in addition to the County permit.

	

	SAMPLING REQUIREMENTS

	A minimum of two soil samples per tank, a minimum 2 feet into native soil, and at least one sample 

for each 20 linear feet of piping must be obtained under the direction of the removal inspector. 

If water is present, water samples may be required. Additional samples may be required.

	Soil samples are to be analyzed by a State approved lab, for contents of the tank and breakdown 

products.  Other analysis may be required.

	Proper sampling techniques and containers are to be used, and containers properly sealed.

Samples are to be transported under proper chain-of-custody. 

	A copy of all sample results shall be submitted to the Yuba County Environmental Health Department-

CUPA within 30 days.

	Minimum verification analysis                                                                           Method

	Total Petroleum Hydrocarbons-Gasoline
	GCFID(5030), GCMS 8260

	Total Petroleum Hydrocarbons-Diesel
	GCFID(3550), GCMS 8260

	Benzene, Toluene, Xylene, Ethylbenzene
	GCPID 8021, GCMS 8260

	Solvents
	GCEC/PID; GC8021

	MTBE, TBA, DIPE, ETBE, TAME, Ethanol, Methanol, 

1,2 DCA, EDB
	GCMS 8260

	Oil and Grease
	1664A

	Metals
	610AA or ICAP

	Pesticides/Creosote
	8081A PCB*PCP*PNA /GCMS8021

	REPORTING REQUIREMENTS

	If the results of the soil sample analysis and/or other criteria, such as site conditions, indicate an

unauthorized release, an Underground Storage Tank Unauthorized Release (Leak)/Contamination Site

Report shall be filed within 5 days by the tank owner. Forms may be obtained from the CUPA. 

	Site investigation and cleanup shall be according to Article 11 of the Underground Storage Tank 

Regulations, and the Tri-regional Guidelines. Oversight agencies shall be the Yuba County and the Environmental Health Department and the Regional Water Quality Control Board.  Workplans shall be approved prior to any work.

	A fee may be charged for cleanup oversight by the CUPA.

	OWNER DECLARATION

	I declare, under penalty of perjury, under the laws of the State of California, that I have read, and I 

understand, and agree to adhere to the requirements of this application to remove underground storage 

tanks.  Furthermore, I will carry out the actions and abide by the provisions as indicated.

	Owner Signature:

	Print Name

	Date:


	FEES

	$1,846.80 plus $256.00 for each additional tank over three.  Remit to:  

Yuba County Environmental Health-CUPA, 915 8th Street, Suite 123, Marysville, CA 95901

(530) 749-5450.    (Make checks payable to Yuba County CDSA)                                                                                                                                                    


[image: image2.png]




